## AX-CTL 1 Loop
One (1) Loop FACP Battery Standby Calculation Chart
Select and fill in all pertinent YELLOW cells/areas | [10 empty] | 0
| Project Name / Location | [9 empty] | SLC QTY |  |  |  | NAC Voltage Drop Calculator - Enter Wiring Distance (+, -)
| Completed by |  |  |  | Date |  |  |  | Detectors |  | SLC#1 |  |  |  |  | Minimum Voltage | Total Current (A) | Wire AWG | Ohms / 1000ft | Wiring Distance (ft) (2-wires [+,-]) | Resistance | Minimum Voltage |  | Detectors | Quiescent | Alarm
[9 empty] | 58000-650ADV | Photoelectric Detector | 0 |  |  |  | NAC#1 Output | 19.4 | 0 | 12 | 2 | 0 | 0 | 19.4 | M6 | Photoelectric Detector | 0.0005 | 0.0005 |  | 5 Minute | 0.083
[9 empty] | 58000-450ADV | Heat Detector | 0 |  |  |  | NAC#2 Output | 19.4 | 0 | 12 | 2 | 0 | 0 | 19.4 | M7 | Heat Detector | 0.0005 | 0.0005 |  | 10 Minute | 0.167
|  |  | Quiescent Current |  |  | Alarm Current |  |  | 58000-750ADV | Multi Sensor Detector | 0 | [11 empty] | M8 | Multi Sensor Detector | 0.0005 | 0.0005 |  | 15 Minute | 0.25
| Equipment | I(A) | X | Total | I(A) | X | Total |  | 58000-550ADV | Ion Detector | 0 |  |  |  | NAC#1 Output | 19.4 | 0 | 14 | 2.6 | 0 | 0 | 19.4 | M9 | Ion Detector | 0.0004 | 0.0004 |  | 20 Minute | 0.334
| Base Card | 0.11 | 1 | 0.11 | 0.195 | 1 | 0.195 |  | XP95 Detector | AX Series Duct Detector | 0 |  |  |  | NAC#2 Output | 19.4 | 0 | 14 | 2.6 | 0 | 0 | 19.4 | M10 | XP95 Detector | 0.00034 | 0.00034 |  | 25 Minute | 0.417
| LCD Backlight Battery Mode "OFF" | 0 | 1 | 0 | 0 | 1 | 0 |  | 45681-800ADV | CO Detector w/Sounder Base | 0 | [11 empty] | M11 | CO Detector w/Sounder Base | 0.0004 | 0.0004 |  | 30 Minute | 0.5
| SLC#1 Current | 0 | 1.25 | 0 | 0 | 1.25 | 0 |  | 0 Amp Required 24VDC Sounder Base Power | [5 empty] | NAC#1 Output | 19.4 | 0 | 16 | 4.2 | 0 | 0 | 19.4 | M12 | -24V Sounder Power |  | 0.033 |  | 35 Minute | 0.584
[9 empty] | Bases |  | 0 |  |  |  | NAC#2 Output | 19.4 | 0 | 16 | 4.2 | 0 | 0 | 19.4 | M13 | Bases |  |  |  | 40 Minute | 0.667
| No Network Card Installed | 0 | 0 | 0 | 0 | 0 | 0 |  | 45681-250ADS | 6" E-Z Fit Base | 0 | [11 empty] | M14 | 6" E-Z Fit Base |  |  |  | 45 Minute | 0.75
| Remote AX-ANN-C (D) | 0.078 | 1 | 0.078 | 0.14 | 1 | 0.14 |  | -LED Output | Remote LED Drive Output | 0 |  |  |  | NAC#1 Output | 19.4 | 0 | 18 | 6.5 | 0 | 0 | 19.4 | M15 | LED Drive Output |  | 0.005 |  | 50 Minute | 0.834
| D9068P DACT w/AX-SEB | 0.109 | 0 | 0 | 0.125 | 0 | 0 |  | MB-SDRT-AA | 4-Wire MultFlex Sounder Base | 0 |  |  |  | NAC#2 Output | 19.4 | 0 | 18 | 6.5 | 0 | 0 | 19.4 | M16 | 4-Wire Multflex Sounder Base | 0.00015 |  |  | 55 Minute | 0.917
| AX-RL8 (8-way relay card) |  |  |  | 0.065 | 0 | 0 |  | 0 Amp Required 24VDC Sounder Base Power | [13 empty] | M17 | -24V Sounder Power |  | 0.017 |  | 60 Minute | 1
| AX-ASW-16 | 0.011 | 0 | 0 | 0.06 | 0 | 0 |  | 45681-242ADS | 4" Relay Base | 0 |  |  |  | Note: Enter total NAC circuit wiring distance from panel to last notification appliance circuit, for Class A | [7 empty] | M18 | 4" Relay Base | 1e-06 | 4e-05
| AX-I/O-48 | 0.011 | 0 | 0 | 0.06 | 0 | 0 |  | 45681-321ADS | Isolating Base | 0 |  |  |  | total distance is wiring out to the devices and back to the FACP. | [7 empty] | M19 | Isolating Base | 3.5e-05 | 3.5e-05
| AX-R10 |  |  |  | 0.13 | 0 | 0 |  | 45681-526 (525)ADS | Sounder Beacon Base (Red/Amber Beacon) | 0 | [11 empty] | M20 | Sounder Beacon Base | 0.0009 | 0.00875 |  | Max Battery | 48
| AX-RL4 | 0.022 | 0 | 0 | 0.1 | 0 | 0 |  | 45681-524 (527)ADS | Enhanced Sounder Beacon Base (Red/Amber) | 0 | [11 empty] | M21 | Enhanced Sounder Beacon Base | 0.0013 | 0.01048
| AX-CTY (no added current draw) | 0 | 0 | 0 | 0 | 0 | 0 |  | Pull Stations | [13 empty] | M22 | Pull Stations
| No ipGateway (AX-LAN) | 0 | 0 | 0 | 0 | 0 | 0 |  | AX-APS2-F1/F2 | Manual Pull Station | 0 | [11 empty] | M23 | Manual Pull Station | 0.0017 | 0.0027
| AX-CZM | 0.12 | 0 | 0 | 0.3 | 0 | 0 |  | 56000-005ADV | Polycarbonate Pull Station | 0 | [11 empty] | M24 | Polycarbonate Pull Station | 0.0002 | 0.0038
[9 empty] | Modules | [13 empty] | M25 | Modules
[9 empty] | 55000-805/806ADV | Monitor Module (Standard and/or Priority) | 0 | [11 empty] | M26 | Monitor Module (Standard and/or Priority) | 0.0006 | 0.0006
[9 empty] | 55000-831ADV | Mini Montior Module (Standard and/or Priority) | 0 | [11 empty] | M27 | Mini Montior Module (Standard and/or Priority) | 0.0006 | 0.005
[9 empty] | 55000-765ADV | Mini Monitor DIN Rail Mount | 0 | [11 empty] | M28 | Mini Monitor DIN Rail Mount | 0.0002 | 0.0036
| Aux 1 (resettable power) | 0.5 |  | 0.5 | 0 |  | 0 |  | 55000-790ADV | Dual Monitor Module | 0 | [11 empty] | M29 | Dual Monitor Module | 0.00085 | 0.00085
| Aux 2 Total (non-resettable power) | 0.14 | [6 empty] | 55000-863ADV | Relay Module | 0 | [11 empty] | M30 | Relay Module | 0.00085 | 0.0035
| -Other Aux 2 power usage | 0 |  | 0 | 0 |  | 0 |  | 55000-820/859ADV | 24VDC and/or 120VAC I/O Module | 0 | [11 empty] | M31 | 24VDC and or 120VAC I/O Module | 0.00095 | 0.003
[9 empty] | 55000-825ADV | NAC (Sounder) Module | 0 | [11 empty] | M32 | NAC (Sounder) Module | 0.001 | 0.001
| NAC#1 Output |  |  |  | 0 |  | 0 |  | Open Area Sounders and Beacons | [13 empty] | M33 | Open Area Sounders and Beacons
| NAC#2 Output |  |  |  | 0 |  | 0 |  | 55000-041(042)ADV | Open Area Sounder (Red or White) | 0 | [11 empty] | M34 | Open Area Sounder | 0.00031 | 0.006
[9 empty] | 58000-011(012)ADV | Open Area Sounder Beacon (Red or White) | 0 | [11 empty] | M35 | Open Area Sounder Beacon | 0.00075 | 0.0084
[9 empty] | 55000-877(879)ADV | Beacon (Base Mount, Red or Amber) | 0 | [11 empty] | M36 | Beacon | 0.00015 | 0.003
| Total | Quiescent Current |  | 0.688 | Alarm Current |  | 0.335 |  | Loop Isolator | [13 empty] | M37 | Loop Isolator
| Standby Duration (hours) = | 24 | Hr | 16.512 | 5 Minute | 0.083 | 0.027805 |  | 55000-750ADV | Isolator Module | 0 | [11 empty] | M38 | Isolator Module | 3.5e-05 | 3.5e-05
|  | → Quiescent Current |  |  |  |  | 16.512 |  | 45681-211ADS | Isolator Base | 0 | [11 empty] | M39 | Isolator Base
|  | Total Load (Quiescent + Alarm) = |  |  |  |  | 16.5398 | [12 empty] | battcalc
|  | Battery Required (includes battery derating factor) = |  |  |  |  | 20.6748 | Ahr | [15 empty] | Aux 2 Current Draw | 0.14
| This Battery Calc form is used for one Loop intelligent Fire Alarm Control Panels; AX-CTL-1, | [7 empty] | # of Active LEDs | 5 | 0 | Amp Quiescent Current | [11 empty] | No Network Card Installed | 0 | 0 | 0
| 1L, 1V, AX-CC1-16 and one loop Modular Command Centers. AV-AMP-80 Battery Calc form | [9 empty] | 0 | Amp Alarm Current | [11 empty] | AX-NET4, Style 4 Network | 0.02 | 0.02 | 1
| must also be utilized for AX-CTL-1V, AX-CC1-16 and Modular Command Centers with audio. | [7 empty] | SLC Warnings: | 0 | [13 empty] | AX-NET7, Style 7 Network | 0.062 | 0.062 | 1
| Notes: | [7 empty] | SLC Intelligent/Addressable Loop Devices |  | OK
[9 empty] | SLC Intelligent/Addressable Loop Current Draw |  | OK
[24 empty] | LCD Backlight Battery Mode "OFF" | 0 | 0
[24 empty] | LCD Backlight Battery Mode "ON" | 0.03 | 0.03
[24 empty] | No ipGateway (AX-LAN) | 0 | 0 | 0
[13 empty] | REV | 04 | [9 empty] | ipGateway (AX-LAN), Style 4 | 0.07 | 0.07 | 1
[24 empty] | ipGateway (AX-LAN), Style 7 | 0.11 | 0.11 | 1
[24 empty] | 123 | 0 | 0 | 0
[24 empty] | 124 | 1 | 1 | 1
[24 empty] | 125 | 1 | 2 | 2
Print AX-CTL 1 Loop
Sheets (3)

## AX-CTL 2 Loop
Two (2) Loop FACP Battery Standby Calculation Chart
Select and fill in all pertinent YELLOW cells/areas | [10 empty] | 0 | 0
| Project Name / Location | [9 empty] | SLC QTY | SLC QTY |  |  |  | NAC Voltage Drop Calculator - Enter Wiring Distance (+, -)
| Completed by |  |  |  | Date |  |  |  | Detectors |  | SLC#1 | SLC#2 |  |  |  |  | Minimum Voltage | Total Current (A) | Wire AWG | Ohms / 1000ft | Wiring Distance (ft) (2-wires [+,-]) | Resistance | Minimum Voltage |  | Detectors | Quiescent | Alarm
[9 empty] | 58000-650ADV | Photoelectric Detector | 0 | 0 |  |  |  | NAC#1 Output | 19.4 | 0 | 12 | 2 | 0 | 0 | 19.4 | M6 | Photoelectric Detector | 0.0005 | 0.0005 |  | 5 Minute | 0.083
[9 empty] | 58000-450ADV | Heat Detector | 0 | 0 |  |  |  | NAC#2 Output | 19.4 | 0 | 12 | 2 | 0 | 0 | 19.4 | M7 | Heat Detector | 0.0005 | 0.0005 |  | 10 Minute | 0.167
|  |  | Quiescent Current |  |  | Alarm Current |  |  | 58000-750ADV | Multi Sensor Detector | 0 | 0 | [11 empty] | M8 | Multi Sensor Detector | 0.0005 | 0.0005 |  | 15 Minute | 0.25
| Equipment | I(A) | X | Total | I(A) | X | Total |  | 58000-550ADV | Ion Detector | 0 | 0 |  |  |  | NAC#1 Output | 19.4 | 0 | 14 | 2.6 | 0 | 0 | 19.4 | M9 | Ion Detector | 0.0004 | 0.0004 |  | 20 Minute | 0.334
| Base Card | 0.11 | 1 | 0.11 | 0.195 | 1 | 0.195 |  | XP95 Detector | AX Series Duct Detector | 0 | 0 |  |  |  | NAC#2 Output | 19.4 | 0 | 14 | 2.6 | 0 | 0 | 19.4 | M10 | XP95 Detector | 0.00034 | 0.00034 |  | 25 Minute | 0.417
| LCD Backlight Battery Mode "OFF" | 0 | 1 | 0 | 0 | 1 | 0 |  | 45681-800ADV | CO Detector w/Sounder Base | 0 | 0 | [11 empty] | M11 | CO Detector w/Sounder Base | 0.0004 | 0.0004 |  | 30 Minute | 0.5
| SLC#1 Current | 0 | 1.25 | 0 | 0 | 1.25 | 0 |  | 0 Amp Required 24VDC Sounder Base Power | [6 empty] | NAC#1 Output | 19.4 | 0 | 16 | 4.2 | 0 | 0 | 19.4 | M12 | -24V Sounder Power |  | 0.033 |  | 35 Minute | 0.584
| SLC#2 Current | 0 | 1.25 | 0 | 0 | 1.25 | 0 |  | Bases | [6 empty] | NAC#2 Output | 19.4 | 0 | 16 | 4.2 | 0 | 0 | 19.4 |  | Bases |  |  |  | 40 Minute | 0.667
| No Network Card Installed | 0 | 0 | 0 | 0 | 0 | 0 |  | 45681-250ADS | 6" E-Z Fit Base | 0 | 0 | [11 empty] | M14 | 6" E-Z Fit Base |  |  |  | 45 Minute | 0.75
| Remote AX-ANN-C (D) | 0.078 | 0 | 0 | 0.14 | 0 | 0 |  | -LED Output | Remote LED Drive Output | 0 | 0 |  |  |  | NAC#1 Output | 19.4 | 0 | 18 | 6.5 | 0 | 0 | 19.4 | M15 | LED Drive Output |  | 0.005 |  | 50 Minute | 0.834
| D9068P DACT w/AX-SEB | 0.109 | 0 | 0 | 0.125 | 0 | 0 |  | MB-SDRT-AA | 4-Wire MultFlex Sounder Base | 0 | 0 |  |  |  | NAC#2 Output | 19.4 | 0 | 18 | 6.5 | 0 | 0 | 19.4 |  | 4-Wire Multflex Sounder Base | 0.00015 |  |  | 55 Minute | 0.917
| AX-RL8 (8-way relay card) |  |  |  | 0.065 | 0 | 0 |  | 0 Amp Required 24VDC Sounder Base Power | [15 empty] | -24V Sounder Power |  | 0.017 |  | 60 Minute | 1
| AX-ASW-16 | 0.011 | 0 | 0 | 0.06 | 0 | 0 |  | 45681-242ADS | 4" Relay Base | 0 | 0 |  |  |  | Note: Enter total NAC circuit wiring distance from panel to last notification appliance circuit, for Class A | [7 empty] | M18 | 4" Relay Base | 1e-06 | 4e-05
| AX-I/O-48 | 0.011 | 0 | 0 | 0.06 | 0 | 0 |  | 45681-321ADS | Isolating Base | 0 | 0 |  |  |  | total distance is wiring out to the devices and back to the FACP. | [7 empty] | M19 | Isolating Base | 3.5e-05 | 3.5e-05
| AX-RL10 |  |  |  | 0.13 | 0 | 0 |  | 45681-526 (525)ADS | Sounder Beacon Base (Red/Amber Beacon) | 0 | 0 | [11 empty] | M20 | Sounder Beacon Base | 0.0009 | 0.00875 |  | Max Battery | 48
| AX-RL4 | 0.022 | 0 | 0 | 0.1 | 0 | 0 |  | 45681-524 (527)ADS | Enhanced Sounder Beacon Base (Red/Amber) | 0 | 0 | [11 empty] | M21 | Enhanced Sounder Beacon Base | 0.0013 | 0.01048
| AX-CTY (no added current draw) | 0 | 0 | 0 | 0 | 0 | 0 |  | Pull Stations |  | 0 | 0 | [11 empty] | M22 | Pull Stations
| No ipGateway (AX-LAN) | 0 | 0 | 0 | 0 | 0 | 0 |  | AX-APS2-F1/F2 | Manual Pull Station | 0 | 0 | [11 empty] | M23 | Manual Pull Station | 0.0017 | 0.0027
| AX-CZM | 0.12 | 0 | 0 | 0.3 | 0 | 0 |  | 56000-005ADV | Polycarbonate Pull Station | 0 | 0 | [11 empty] | M24 | Polycarbonate Pull Station | 0.0002 | 0.0038
[9 empty] | Modules | [14 empty] | M25 | Modules
[9 empty] | 55000-805/806ADV | Monitor Module (Standard and/or Priority) | 0 | 0 | [12 empty] | Monitor Module (Standard and/or Priority) | 0.0006 | 0.0006
[9 empty] | 55000-831ADV | Mini Montior Module (Standard and/or Priority) | 0 | 0 | [11 empty] | M27 | Mini Montior Module (Standard and/or Priority) | 0.0006 | 0.005
[9 empty] | 55000-765ADV | Mini Monitor DIN Rail Mount | 0 | 0 | [11 empty] | M28 | Mini Monitor DIN Rail Mount | 0.0002 | 0.0036
| Aux 1 (resettable power) | 0 |  | 0 | 0 |  | 0 |  | 55000-790ADV | Dual Monitor Module | 0 | 0 | [11 empty] | M29 | Dual Monitor Module | 0.00085 | 0.00085
| Aux 2 Total (non-resettable power) | 0 | [6 empty] | 55000-863ADV | Relay Module | 0 | 0 | [11 empty] | M30 | Relay Module | 0.00085 | 0.0035
| -Other Aux 2 power usage | 0 |  | 0 | 0 |  | 0 |  | 55000-820/859ADV | 24VDC and/or 120VAC I/O Module | 0 | 0 | [11 empty] | M31 | 24VDC and or 120VAC I/O Module | 0.00095 | 0.003
[9 empty] | 55000-825ADV | NAC (Sounder) Module | 0 | 0 | [11 empty] | M32 | NAC (Sounder) Module | 0.001 | 0.001
| NAC#1 Output |  |  |  | 0 |  | 0 |  | Open Area Sounders and Beacons | [14 empty] | M33 | Open Area Sounders and Beacons
| NAC#2 Output |  |  |  | 0 |  | 0 |  | 55000-041(042)ADV | Open Area Sounder (Red or White) | 0 | 0 | [11 empty] | M34 | Open Area Sounder | 0.00031 | 0.006
[9 empty] | 58000-011(012)ADV | Open Area Sounder Beacon (Red or White) | 0 | 0 | [11 empty] | M35 | Open Area Sounder Beacon | 0.00075 | 0.0084
[9 empty] | 55000-877(879)ADV | Beacon (Base Mount, Red or Amber) | 0 | 0 | [11 empty] | M36 | Beacon | 0.00015 | 0.003
| Total | Quiescent Current |  | 0.11 | Alarm Current |  | 0.195 |  | Loop Isolator | [14 empty] | M37 | Loop Isolator
| Standby Duration (hours) = | 24 | Hr | 2.64 | 5 Minute | 0.083 | 0.016185 |  | 55000-750ADV | Isolator Module | 0 | 0 | [11 empty] | M38 | Isolator Module | 3.5e-05 | 3.5e-05
|  | → Quiescent Current |  |  |  |  | 2.64 |  | 45681-211ADS | Isolator Base | 0 | 0 | [11 empty] | M39 | Isolator Base
|  | Total Load (Quiescent + Alarm) = |  |  |  |  | 2.6562 | [13 empty] | battcalc |  |  | M40
|  | Battery Required (includes battery derating factor) = |  |  |  |  | 3.3202 | Ahr | [16 empty] | Aux 2 Current Draw | 0
| This Battery Calc form is used for two Loop intelligent Fire Alarm Control Panels; AX-CTL-2, | [7 empty] | # of Active LEDs/Loop | 5 | 0 | 0 | Amp Quiescent Current | [11 empty] | No Network Card Installed | 0 | 0 | 0
| 2V, AX-CC2-16 and two loop Modular Command Centers. AV-AMP-80 Battery Calc form must | [9 empty] | 0 | 0 | Amp Alarm Current | [11 empty] | AX-NET4, Style 4 Network | 0.02 | 0.02 | 1
| also be utilized for AX-CTL-2V, AX-CC2-16 and Modular Command Centers with audio. | [7 empty] | SLC Warnings: | 0 | 0 | [13 empty] | AX-NET7, Style 7 Network | 0.062 | 0.062 | 1
| Notes: | [7 empty] | SLC Intelligent/Addressable Loop Devices |  | OK | OK
[9 empty] | SLC Intelligent/Addressable Loop Current Draw |  | OK | OK
[25 empty] | LCD Backlight Battery Mode "OFF" | 0 | 0
[25 empty] | LCD Backlight Battery Mode "ON" | 0.03 | 0.03
[25 empty] | No ipGateway (AX-LAN) | 0 | 0 | 0
[14 empty] | REV | 04 | [9 empty] | ipGateway (AX-LAN), Style 4 | 0.07 | 0.07 | 1
[25 empty] | ipGateway (AX-LAN), Style 7 | 0.11 | 0.11 | 1
[25 empty] | 123 | 0 | 0 | 0
[25 empty] | 124 | 1 | 1 | 1
[25 empty] | 125 | 1 | 2 | 2
Print AX-CTL 2 Loop
Sheets (3)

## AX-CTL 4 Loop
Four (4) Loop FACP Battery Standby Calculation Chart
Select and fill in all pertinent YELLOW cells/areas | [10 empty] | 0 | 0 | 0 | 0
| Project Name / Location | [9 empty] | SLC QTY | SLC QTY | SLC QTY | SLC QTY |  |  |  | NAC Voltage Drop Calculator - Enter Wiring Distance (+, -)
| Completed by |  |  |  | Date |  |  |  | Detectors |  | SLC#1 | SLC#2 | SLC#3 | SLC#4 |  |  |  |  | Minimum Voltage | Total Current (A) | Wire AWG | Ohms / 1000ft | Wiring Distance (ft) (2-wires [+,-]) | Resistance | Minimum Voltage |  | Detectors | Quiescent | Alarm
[9 empty] | 58000-650ADV | Photoelectric Detector | 0 | 0 | 0 | 0 |  |  |  | NAC#1 Output | 19.4 | 0 | 12 | 2 | 0 | 0 | 19.4 | M6 | Photoelectric Detector | 0.0005 | 0.0005 |  | 5 Minute | 0.083
[9 empty] | 58000-450ADV | Heat Detector | 0 | 0 | 0 | 0 |  |  |  | NAC#2 Output | 19.4 | 0 | 12 | 2 | 0 | 0 | 19.4 | M7 | Heat Detector | 0.0005 | 0.0005 |  | 10 Minute | 0.167
|  |  | Quiescent Current |  |  | Alarm Current |  |  | 58000-750ADV | Multi Sensor Detector | 0 | 0 | 0 | 0 | [11 empty] | M8 | Multi Sensor Detector | 0.0005 | 0.0005 |  | 15 Minute | 0.25
| Equipment | I(A) | X | Total | I(A) | X | Total |  | 58000-550ADV | Ion Detector | 0 | 0 | 0 | 0 |  |  |  | NAC#1 Output | 19.4 | 0 | 14 | 2.6 | 0 | 0 | 19.4 | M9 | Ion Detector | 0.0004 | 0.0004 |  | 20 Minute | 0.334
| Base Card | 0.11 | 1 | 0.11 | 0.195 | 1 | 0.195 |  | XP95 Detector | AX Series Duct Detector | 0 | 0 | 0 | 0 |  |  |  | NAC#2 Output | 19.4 | 0 | 14 | 2.6 | 0 | 0 | 19.4 | M10 | XP95 Detector | 0.00034 | 0.00034 |  | 25 Minute | 0.417
| LCD Backlight Battery Mode "OFF" | 0 | 1 | 0 | 0 | 1 | 0 |  | 45681-800ADV | CO Detector w/Sounder Base | 0 | 0 | 0 | 0 | [11 empty] | M11 | CO Detector w/Sounder Base | 0.0004 | 0.0004 |  | 30 Minute | 0.5
| SLC#1 Current | 0 | 1.25 | 0 | 0 | 1.25 | 0 |  | 0 Amp Required 24VDC Sounder Base Power | [8 empty] | NAC#1 Output | 19.4 | 0 | 16 | 4.2 | 0 | 0 | 19.4 | M12 | -24V Sounder Power |  | 0.033 |  | 35 Minute | 0.584
| SLC#2 Current | 0 | 1.25 | 0 | 0 | 1.25 | 0 |  | Bases | [8 empty] | NAC#2 Output | 19.4 | 0 | 16 | 4.2 | 0 | 0 | 19.4 | M13 | Bases |  |  |  | 40 Minute | 0.667
| SLC#3 Current | 0 | 1.25 | 0 | 0 | 1.25 | 0 |  | 45681-250ADS | 6" E-Z Fit Base | 0 | 0 | 0 | 0 | [11 empty] | M14 | 6" E-Z Fit Base |  |  |  | 45 Minute | 0.75
| SLC#4 Current | 0 | 1.25 | 0 | 0 | 1.25 | 0 |  | -LED Output | Remote LED Drive Output | 0 | 0 | 0 | 0 |  |  |  | NAC#1 Output | 19.4 | 0 | 18 | 6.5 | 0 | 0 | 19.4 | M15 | LED Drive Output |  | 0.005 |  | 50 Minute | 0.834
| No Network Card Installed | 0 | 0 | 0 | 0 | 0 | 0 |  | MB-SDRT-AA | 4-Wire MultFlex Sounder Base | 0 | 0 | 0 | 0 |  |  |  | NAC#2 Output | 19.4 | 0 | 18 | 6.5 | 0 | 0 | 19.4 | M16 | 4-Wire Multflex Sounder Base | 0.00015 |  |  | 55 Minute | 0.917
| Remote AX-ANN-C (D) | 0.078 | 0 | 0 | 0.14 | 0 | 0 |  | 0 Amp Required 24VDC Sounder Base Power | [16 empty] | M17 | -24V Sounder Power |  | 0.017 |  | 60 Minute | 1
| D9068P DACT w/AX-SEB | 0.109 | 0 | 0 | 0.125 | 0 | 0 |  | 45681-242ADS | 4" Relay Base | 0 | 0 | 0 | 0 | [11 empty] | M18 | 4" Relay Base | 1e-06 | 4e-05
| AX-RL8 (8-way relay card) |  |  |  | 0.065 | 0 | 0 |  | 45681-321ADS | Isolating Base | 0 | 0 | 0 | 0 |  |  |  | NAC#3 Output | 19.4 | 0 | 12 | 2 | 0 | 0 | 19.4 | M19 | Isolating Base | 3.5e-05 | 3.5e-05
| AX-ASW-16 | 0.011 | 0 | 0 | 0.06 | 0 | 0 |  | 45681-526 (525)ADS | Sounder Beacon Base (Red/Amber Beacon) | 0 | 0 | 0 | 0 |  |  |  | NAC#4 Output | 19.4 | 0 | 12 | 2 | 0 | 0 | 19.4 | M20 | Sounder Beacon Base | 0.0009 | 0.00875 |  | Max Battery | 48
| AX-I/O-48 | 0.011 | 0 | 0 | 0.06 | 0 | 0 |  | 45681-524 (527)ADS | Enhanced Sounder Beacon Base (Red/Amber) | 0 | 0 | 0 | 0 | [11 empty] | M21 | Enhanced Sounder Beacon Base | 0.0013 | 0.01048
| AX-RL10 |  |  |  | 0.13 | 0 | 0 |  | Pull Stations | [8 empty] | NAC#3 Output | 19.4 | 0 | 14 | 2.6 | 0 | 0 | 19.4 | M22 | Pull Stations
| AX-RL4 | 0.22 | 0 | 0 | 0.1 | 0 | 0 |  | AX-APS2-F1/F2 | Manual Pull Station | 0 | 0 | 0 | 0 |  |  |  | NAC#4 Output | 19.4 | 0 | 14 | 2.6 | 0 | 0 | 19.4 | M23 | Manual Pull Station | 0.0017 | 0.0027
| AX-CTY (no added current draw) | 0 | 0 | 0 | 0 | 0 | 0 |  | 56000-005ADV | Polycarbonate Pull Station | 0 | 0 | 0 | 0 | [11 empty] | M24 | Polycarbonate Pull Station | 0.0002 | 0.0038
| No ipGateway (AX-LAN) | 0 | 0 | 0 | 0 | 0 | 0 |  | Modules | [8 empty] | NAC#3 Output | 19.4 | 0 | 16 | 4.2 | 0 | 0 | 19.4 | M25 | Modules
| AX-CZM | 0.12 | 0 | 0 | 0.3 | 0 | 0 |  | 55000-805/806ADV | Monitor Module (Standard and/or Priority) | 0 | 0 | 0 | 0 |  |  |  | NAC#4 Output | 19.4 | 0 | 16 | 4.2 | 0 | 0 | 19.4 | M26 | Monitor Module (Standard and/or Priority) | 0.0006 | 0.0006
[9 empty] | 55000-831ADV | Mini Montior Module (Standard and/or Priority) | 0 | 0 | 0 | 0 | [11 empty] | M27 | Mini Montior Module (Standard and/or Priority) | 0.0006 | 0.005
[9 empty] | 55000-765ADV | Mini Monitor DIN Rail Mount | 0 | 0 | 0 | 0 |  |  |  | NAC#3 Output | 19.4 | 0 | 18 | 6.5 | 0 | 0 | 19.4 | M28 | Mini Monitor DIN Rail Mount | 0.0002 | 0.0036
[9 empty] | 55000-790ADV | Dual Monitor Module | 0 | 0 | 0 | 0 |  |  |  | NAC#4 Output | 19.4 | 0 | 18 | 6.5 | 0 | 0 | 19.4 | M29 | Dual Monitor Module | 0.00085 | 0.00085
| Aux 1 (resettable power) | 0 |  | 0 | 0 |  | 0 |  | 55000-863ADV | Relay Module | 0 | 0 | 0 | 0 | [11 empty] | M30 | Relay Module | 0.00085 | 0.0035
| Aux 2 Total (non-resettable power) | 0 | [6 empty] | 55000-820/859ADV | 24VDC and/or 120VAC I/O Module | 0 | 0 | 0 | 0 |  |  |  | Note: Enter total NAC circuit wiring distance from panel to last notification appliance circuit, for Class A | [7 empty] | M31 | 24VDC and or 120VAC I/O Module | 0.00095 | 0.003
| -Other Aux 2 power usage | 0 |  | 0 | 0 |  | 0 |  | 55000-825ADV | NAC (Sounder) Module | 0 | 0 | 0 | 0 |  |  |  | total distance is wiring out to the devices and back to the FACP. | [7 empty] | M32 | NAC (Sounder) Module | 0.001 | 0.001
| NAC#1 Output |  |  |  | 0 |  | 0 |  | Open Area Sounders and Beacons | [16 empty] | M33 | Open Area Sounders and Beacons
| NAC#2 Output |  |  |  | 0 |  | 0 |  | 55000-041(042)ADV | Open Area Sounder (Red or White) | 0 | 0 | 0 | 0 | [11 empty] | M34 | Open Area Sounder | 0.00031 | 0.006
| NAC#3 Output |  |  |  | 0 |  | 0 |  | 58000-011(012)ADV | Open Area Sounder Beacon (Red or White) | 0 | 0 | 0 | 0 | [11 empty] | M35 | Open Area Sounder Beacon | 0.00075 | 0.0084
| NAC#4 Output |  |  |  | 0 |  | 0 |  | 55000-877(879)ADV | Beacon (Base Mount, Red or Amber) | 0 | 0 | 0 | 0 | [11 empty] | M36 | Beacon | 0.00015 | 0.003
| Total | Quiescent Current |  | 0.11 | Alarm Current |  | 0.195 |  | Loop Isolator | [16 empty] | M37 | Loop Isolator
| Standby Duration (hours) = | 24 | Hr | 2.64 | 5 Minute | 0.083 | 0.016185 |  | 55000-750ADV | Isolator Module | 0 | 0 | 0 | 0 | [11 empty] | M38 | Isolator Module | 3.5e-05 | 3.5e-05
|  | → Quiescent Current |  |  |  |  | 2.64 |  | 45681-211ADS | Isolator Base | 0 | 0 | 0 | 0 | [11 empty] | M39 | Isolator Base
|  | Total Load (Quiescent + Alarm) = |  |  |  |  | 2.6562 | [15 empty] | battcalc
|  | Battery Required (includes battery derating factor) = |  |  |  |  | 3.3202 | Ahr | [18 empty] | Aux 2 Current Draw | 0
| This Battery Calc form is used for four Loop intelligent Fire Alarm Control Panels; AX-CTL-4, | [7 empty] | # of Active LEDs/Loop | 5 | 0 | 0 | 0 | 0 | Amp Quiescent Current | [11 empty] | No Network Card Installed | 0 | 0 | 0
| 4V, AX-CC4-16 and four loop Modular Command Centers. AV-AMP-80 Battery Calc form must | [9 empty] | 0 | 0 | 0 | 0 | Amp Alarm Current | [11 empty] | AX-NET4, Style 4 Network | 0.02 | 0.02 | 1
| also be utilized for AX-CTL-4V, AX-CC4-16 and Modular Command Centers with audio. | [7 empty] | SLC Warnings: | 0 | 0 | 0 | 0 | [13 empty] | AX-NET7, Style 7 Network | 0.062 | 0.062 | 1
| Notes: | [7 empty] | SLC Intelligent/Addressable Loop Devices |  | OK | OK | OK | OK
[9 empty] | SLC Intelligent/Addressable Loop Current Draw |  | OK | OK | OK | OK
[27 empty] | LCD Backlight Battery Mode "OFF" | 0 | 0
[27 empty] | LCD Backlight Battery Mode "ON" | 0.03 | 0.03
[27 empty] | No ipGateway (AX-LAN) | 0 | 0 | 0
[16 empty] | REV | 04 | [9 empty] | ipGateway (AX-LAN), Style 4 | 0.07 | 0.07 | 1
[27 empty] | ipGateway (AX-LAN), Style 7 | 0.11 | 0.11 | 1
[27 empty] | 123 | 0 | 0 |  |  |  | 0
[27 empty] | 124 | 1 | 1 |  |  |  | 1
[27 empty] | 125 | 1 | 2 |  |  |  | 2
Print AX-CTL 4 Loop
Sheets (3)

## AV-AMP-80
AV-AMP-80 Amplifier Battery Standby Calculation Chart
[11 empty] | 5 Minute | 0.083
Select and fill in all pertinent YELLOW cells/areas | [10 empty] | 10 Minute | 0.167
| Project | [9 empty] | 15 Minute | 0.25
| Completed by |  |  |  | Date | [5 empty] | 20 Minute | 0.334
[11 empty] | 25 Minute | 0.417
[11 empty] | 30 Minute | 0.5
|  |  | Quiescent Current |  |  | Alarm Current |  |  |  |  | 35 Minute | 0.584
| Equipment | I(A) | X | Total | I(A) | X | Total |  |  |  | 40 Minute | 0.667
| AV-AMP-80 | 0.035 | 1 | 0.035 | 0.22 | 1 | 0.22 |  |  |  | 45 Minute | 0.75
[11 empty] | 50 Minute | 0.834
[11 empty] | 55 Minute | 0.917
| Optional Current Draw | 0 | 1 | 0 | 0 | 1 | 0 |  |  |  | 60 Minute | 1
| Amplifier 1 (Maximum 40 Watts) | Enter Circuit Wattage |  | 0 | 0 |  | 0
| Amplifier 2 (Maximum 40 Watts) |  |  | 0 | 0 |  | 0
| Total | Quiescent Current |  | 0.035 | Alarm Current |  | 0.22 |  |  |  | Max Battery | 48
| Standby Duration (hours) = | 24 | Hr | 0.84 | 5 Minute | 0.083 | 0.01826
|  | → Quiescent Current |  |  |  |  | 0.84
|  | Total Load (Quiescent + Alarm) = |  |  |  |  | 0.85826
|  | Battery Required (includes battery derating factor) = |  |  |  |  | 1.0728 | Ahr
This Battery Calc form is used for the AV-AMP-80 Audio Amplifer used
| in AX-CTL-1V, 2V, 4V, AX-CC[x]-16 and Modular Command Centers. |  |  |  |  | AX-PSU-6: |  | OK
Notes:
[9 empty] | REV | 03
Note: If powering any additional options from the AV-AMP-80 Power Supply (AX-PSU-6) remember to add Quiescent and Alarm Currents
Do not exceed 5 Amp Max. on the AX-PSU-6
Print AV-AMP-80
Sheet

## AV-VB
AV-VB Audio Booster Battery Standby Calculation Chart
Select and fill in all pertinent YELLOW cells/areas | [10 empty] | 5 Minute | 0.083
| Project | [9 empty] | 10 Minute | 0.167
| Completed by |  |  |  | Date | [5 empty] | 15 Minute | 0.25
[11 empty] | 20 Minute | 0.334
[11 empty] | 25 Minute | 0.417
|  |  | Quiescent Load |  |  | Fire Alarm Load |  |  |  |  | 30 Minute | 0.5
| Equipment | I(A) | X | Total | I(A) | X | Total |  |  |  | 35 Minute | 0.584
| AV-AMP-80 | 0.035 | 1 | 0.035 | 0.22 | 1 | 0.22 |  |  |  | 40 Minute | 0.667
| Optional Current Draw | 0 | 1 | 0 | 0 | 1 | 0 |  |  |  | 45 Minute | 0.75
[11 empty] | 50 Minute | 0.834
[11 empty] | 55 Minute | 0.917
| Amplifier 1 (Maximum 40 Watts) | Enter Circuit Wattage |  | 0 | 0 |  | 0 |  |  |  | 60 Minute | 1
| Amplifier 2 (Maximum 40 Watts) |  |  | 0 | 0 |  | 0
| Total | ΣQuiescent Load |  | 0.035 | ΣAlarm Load |  | 0.22
| Standby Duration (hours) = | 24 | Hr | 0.84 | 5 Minute | 0.083 | 0.01826
[5 empty] | → (carry forward) + |  | 0.84 |  |  |  | Max Battery | 48
[6 empty] | Total Load (Quiescent + Alarm) = | 0.85826
|  | Battery Required (includes battery derating factor) = |  |  |  |  | 1.0728 | Ahr
| This Battery Calc form is used for the AV-VB Audio Booster |  |  |  |  | AX-PSU-6: |  | OK
Notes:
[9 empty] | REV | 03
Note: If powering any additional options from the AV-AMP-80 Power Supply (AX-PSU-6) remember to add Quiescent and Alarm Currents
Do not exceed 5 Amp Max. on the AX-PSU-6
Print AV-VB
Sheet

## AV-TEL
Firefighter Phone Product Battery Standby Calculation Chart
Select and fill in all pertinent YELLOW cells/areas
| Project | [9 empty] | 5 Minute | 0.083
| Completed by |  |  |  | Date | [5 empty] | 10 Minute | 0.167
[11 empty] | 15 Minute | 0.25
[11 empty] | 20 Minute | 0.334
|  |  | Quiescent Load |  |  | Active Load |  |  |  |  | 25 Minute | 0.417
| Telephone Equipment | I(A) | X | Total | I(A) | X | Total |  |  |  | 30 Minute | 0.5
| AV-TEL Controlled Phones | 0.015 | 0 | 0 | 0.015 | 0 | 0 |  |  |  | 35 Minute | 0.584
| AV-JACK/AV-TEL-SUP/AV-CTEL | 0.0057 | 0 | 0 | 0.09 | 0 | 0 |  |  |  | 40 Minute | 0.667
[11 empty] | 45 Minute | 0.75
| AV-TEL-RISER6 Controlled Phones | 0.05 | 0 | 0 | 0.05 | 0 | 0 |  |  |  | 50 Minute | 0.834
| # of Command Center Phones (Max. 2) | 0.015 | 0 | 0 | 0.015 | 0 | 0 |  |  |  | 55 Minute | 0.917
| AV-JACK/AV-TEL-SUP/AV-CTEL | 0.0057 | 0 | 0 | 0.09 | 0 | 0 |  |  |  | 60 Minute | 1
| Total | ΣQuiescent Load |  | 0 | ΣAlarm Load |  | 0
| Standby Duration (hours) = | 24 | Hr | 0 | 5 Minute | 0.083 | 0
[5 empty] | → (carry forward) + |  | 0
[6 empty] | Total Load (Quiescent + Active) = | 0
|  | Battery Required (includes battery derating factor) = |  |  |  |  | 0 | Ahr
This Battery Calc form is used for the Advanced Firefighter Phone Products
Notes:
[9 empty] | REV | 01
Print Firefighter
Phone Sheet

## AX-PSU-6
AX-PSU-6 Power Supply/Charger Battery Standby Calculation Chart
Select and fill in all pertinent YELLOW cells/areas | [10 empty] | 5 Minute | 0.083
| Project | [9 empty] | 10 Minute | 0.167
| Completed by |  |  |  | Date | [5 empty] | 15 Minute | 0.25
[11 empty] | 20 Minute | 0.334
[11 empty] | 25 Minute | 0.417
|  |  | Quiescent Load |  |  | Fire Alarm Load |  |  |  |  | 30 Minute | 0.5
| Equipment | [9 empty] | 35 Minute | 0.584
|  | 0 |  |  | 0 | [5 empty] | 40 Minute | 0.667
|  | 0 |  |  | 0 | [5 empty] | 45 Minute | 0.75
|  | 0 |  |  | 0 | [5 empty] | 50 Minute | 0.834
|  | 0 |  |  | 0 | [5 empty] | 55 Minute | 0.917
|  | 0 |  |  | 0 | [5 empty] | 60 Minute | 1
| Total | ΣQuiescent Load |  | 0 | ΣAlarm Load |  | 0
| Standby Duration (hours) = | 24 | Hr | 0 | 5 Minute | 0.083 | 0
[5 empty] | → (carry forward) + |  | 0
[6 empty] | Total Load (Quiescent + Alarm) = | 0
|  | Battery Required (includes battery derating factor) = |  |  |  |  | 0 | Ahr |  |  | Max Battery | 48
| This Battery Calc form is used for AX-PSU Power suply requirements |  |  |  |  | AX-PSU-6: |  | OK
Notes:
[9 empty] | REV | 01
Note: The AX-PSU-6 power supply/charge can supply up to 5 Amps of power for fire alarm installation usage. In the above chart, add Quiescent and
Alarm Currents as required, remembering not exceed the 5 Amp Max. In addition, the AX-PSU-6 provides the charging for the required batteries.
Print AX-PSU-6
Sheet